- SCOPE

- This specification in combination with Pump Data Sheets and Material Requisition specification identifies the minimum requirements for metallic, lined sealless magnetic drive centrifugal pumps, drivers and accessories.

- REFERENCE CODES AND STANDARDS

- Pumps shall comply with the latest editions of the following codes and standards as specified herein:

ANSI  B73.1M

ANSI  B16.5

Hydraulic Institute Standards

National Electric Code (NEC)

OSHA Rules and Regulations

- DEFINITIONS

3.1	Non-metallic, lined magnetic drive pumps utilize ductile cast iron outer shell with injection molded liner and encapsulated inner rotating assembly including a set of inner magnets within a containment shell or rear casing.  Inner magnets are magnetically coupled or driven by outer magnet ring or drive magnet coupled to a conventional drive motor.  Liquid end is hermetically sealed by static o-ring or gasket(s).

3.2	Close-coupled drivers are conventional drivers mounted directly to pumps frame.  No base, coupling or guards are required for this mounting style.

3.3	Non-contact bearing/magnet system includes oversized drive and driven magnet set positioned such that reverse axial thrusting is reduced during adverse operating conditions minimizing contact of reverse axial thrust collars.  This prevents contact of parts that close off circulation of air or fluid between radial bearing and pump shaft.  Radial bearing is also positioned forward to maximize exposure to fluid/air circulation reducing frictional heat generation.

- GENERAL DESIGN

4.1	Pumps shall be non-metallic, lined magnetic drive type, 150# flanged suction and discharge connections, close-coupled configuration, Iwaki America MDM design with patented impeller mounting system and non-contact bearing/magnet system, or pre-approved equal, as specified in the data sheet.

4.2	Pumps shall have foot mounted front casing designs.

4.3	Pumps shall comply with applicable sections of Hydraulic Institute Standards, ANSI B16.5 flange standards, and ANSI B73.1 dimensional standards unless otherwise noted.

4.4	Pump casings and internal liquid passages shall be self-venting and self-draining.

4.4	Pumps, drivers and accessories shall be suitable for continuous operation at the specified operating conditions, and at flows ranging from the specified minimum flow to end of curve conditions.

4.5	Pump head-capacity curve characteristics shall rise continuously from rated capacity to specified minimum flow.  Pump rated capacity shall not exceed capacity at the best efficiency point.  Pump design and selection shall permit a 5% head increase at rated flow by installing a new impeller unless otherwise noted.

4.6	Required Net Positive Suction Head (NPSHr) shall be based on water.  Available NPSHa shall exceed required NPSHr by a minimum of two feet.

4.7	Any electrical drives or accessories shall be suitable for the specified electrical area classification.

4.8	Noise emission shall not exceed 85 dBA, 3 ft. from equipment surfaces.

- CASINGS

  - Front casing covers shall be constructed of ductile cast iron and separable from front casing liner.  Front casing liners shall be single piece, injection molded designs with flat faced flanges, made of CFR-ETFE or virgin PFA and will utilize a fully confined PTFE envelope gasket for sealing between pump casing and containment shell.  Front casing shall include integrally molded front shaft support with three individual support members.  Support members shall have rounded edges and circular shape for maximum strength and minimum resistance to inlet flow. Pump pressure casings shall be designed for specified casing design pressures, temperatures and hydrostatic test pressures.  Pressure casings include front casing cover and liner and containment shell and containment shell covers.

  - Front casings shall have a flanged drain with PTFE gasket.

- IMPELLERS

6.1	Impellers shall be closed design and include provisions for replaceable forward axial thrust ring and shall be made of CFR-ETFE or PFA. Impeller shall utilize pinned/splined technology allowing for individual replacement of impeller or inner magnet or driven magnet assembly.  Impellers shall have receptacles for two reusable PFA impeller pins.  Impellers shall include balance holes for axial thrust balancing.

- BEARINGS

7.1	The radial bearing shall be a one-piece design press fit into driven or inner magnet.  The outside diameter of the bearing shall have two anti-rotation flats.  The inside diameter of the bearing shall have rifled lubrication/flush grooves.  Bearings shall be High Density Carbon, Silicon Carbide or approved equal.

7.2	The front thrust bearing system shall consist of a two collar design with a replaceable axial thrust surface located on the impeller.  The thrust collars shall be positioned on the adjoining mounting surfaces of the impeller and casing cover.  Each collar will have an anti-rotation shape.  Inboard thrust bearing material shall be PTFE, Silicon Carbide or approved equal, outboard thrust collar material shall be high purity Alumina Ceramic, Silicon Carbide or approved equal.

7.3	The rear thrust bearing system shall consist of a two-collar design with replaceable axial thrust surfaces.  The thrust collars shall be positioned on the adjoining mounting surfaces of the containment shell and inner magnet. Inboard thrust bearing material shall be Silicon Carbide, high purity Alumina Ceramic or approved equal.  Outboard rear thrust bearing material shall be filled or unfilled PTFE.

- PUMP SHAFT

8.1	The pump shaft shall be uniform in diameter and include drilled center for maximum strength and resistance to thermal shock.  The shaft shall have two anti-rotation/positioning flats for securing rear outboard thrust collar in the containment shell as well as positioning shaft in the containment shell.  The shaft material shall be Silicon Carbide or high purity Alumina Ceramic.

- DIVEN MAGNET

9.1	The driven magnet shall be fully encapsulated with CFR-ETFE or virgin PFA as specified.  The bore of the inner magnet shall have two anti-rotation/positioning flats that correspond to the shape of the press fit radial bearing.  The magnet capsule shall accept splinned impeller and include two impeller pin holes for securing impeller to magnet capsule in both radial and axial directions.  Pins shall be held in place by radial bearing.  Magnet capsule shall include anti-rotation shaped seat for inboard rear thrust collar.  Magnet material shall be Samarium Cobalt.

- CONTAINMENT SHELL/COVER

9.1	The Containment shell shall be one piece design constructed of CFR-ETFE or virgin PFA.  The containment shell cover shall be of one piece design constructed of fiber reinforced plastic.  The containment shell and cover assembly shall be supported by a ductile cast iron containment shell support flange.

- DRIVE MAGNET

10.1	The drive or outer magnet shall be dynamically balanced and be capable of mounting directly to standard NEMA motors for close-coupled designs.

- FRAME

11.1	The motor frame adapter shall allow for mounting of  standard NEMA C-faced motors.  Frames shall be ductile cast iron construction.  Design shall allow for either removal of drive and frame while line pressure is maintained, or removal of drive, frame and containment shell support while front casing remains installed in piping system.

- DRIVERS

12.1	Driver nameplate horsepower, not including the service factor, shall be equal to, or exceed the required pump horsepower over the entire performance curve for the design impeller unless otherwise noted.

12.2	Required pump BHP will included corrections for product specific gravity and viscosity.

12.3	All magnetic drive couplings shall have torque ratings greater than or equal to the maximum motor torque the driver is rated for.

- PROTECTIVE INSTRUMENTATION

13.1	If specified, vendors shall supply one or more of the following sensing devices for pump protection;

Containment shell leak detector

Motor current sensor

Motor load sensor

- SHOP TESTS

14.1	All pressure casings shall be hydrostatically tested to manufacturer’s standards.

14.2	All pumps shall be given manufacturer’s standard performance test.

14.3	If specified, performance tests shall be conducted according to Hydraulic Institute Standards, level B acceptance criteria.  Certified test reports shall be available if required.